## Slide 1: Preparatory analysis for brace model
防災科学技術研究所
兵庫耐震工学研究センター
研究員 山下 拓三

## Slide 2: Summary
Simulation plan corresponding to construction order is required. That is, installation of brace should be done after self loading analysis. Here, soundness of brace is investigated for the case not applying gravity(or self load).
It is found that stiffeners are required for reinforcing gusset plate of brace to keep soundness.
Results of push-over analysis are provided. Adequate difference of stiffness between the models with and without brace is confirmed for the braces of M14

## Slide 3: Mass of specimen
 | Volume [mm3] | Mass [kg]
Specimen（floor is reinforced） | 2.24E+08 | 1757
1st layer（not including base plate） | 7.95E+07 | 624
2nd layer | 7.91E+07 | 621
3rd and 4th layer | 6.43E+07 | 504
1st layer
（base plate is not included）
2nd layer
3rd and 4th layer
* Calculated from the data of numerical model

## Slide 4: Analysis case
name | brace | Weight | Diameter of brace | Self load | memo
Case3 | No | H26 experiment |  |  | Not shown in this ppt
Case5 | Yes (No reinforcement on gusset plate) | H26 experiment | M14 | No | 
 |  |  |  | Yes | 
Case3_1 | No | H28 experiment | --- | Yes | 
Case5_1 | Yes (reinforcement on gusset plate) | H28 experiment | M14 | Yes | 
 |  |  | M14 | No | 
 |  |  | M16 | No | 
 |  |  | M20 | No | 

## Slide 5: Weight of Case3（ used for 2-DOF model）
M2
M1
M1
M2
 | 体積 [mm3] | 質量 [kg]
M0 | 9.083e+06 | 71.3
M1 | 4.184e+08 | 3284.4
M2 | 1.252e+09 | 9828.2
M | 1.679e+09 | 13180.2
M0
M=M0+M1+M2
参考資料
このスライドのデータは用いない

## Slide 6: Weight of Case3_1（used for 2-DOF model）
M2
M1
M1
M2
 | 体積 [mm3] | 質量 [kg]
M0 | 9.083e+06 | 71.3
M1 | 4.414E+08 | 3465.0
M2 | 1.327E+09 | 10417.0
M | 1.777E+09 | 13949.5
M0
M=M0+M1+M2

## Slide 7: Static earthquake load
Virtual node which load is applied to
Virtual node and nodes on the section of columns are connected by using “InterpolationConstraintElement”
(the same way used in 10RC)
 | T | Rt | Floor | load[kN] | Sum [kN] | α_i | A_i | C_i | Q_i[kN] | F_i[kN]
case3 | 0.214 | 1.0 | M2 | 96.8 | 96.8 | 0.722 | 1.119 | 0.224 | 21.65 | 21.65
 |  |  | M1 | 32.8 | 129.5 | 0.966 | 1.013 | 0.203 | 26.25 | 4.60
 |  |  | M0 | 4.5 | 134.1 | 1.000 | 1.000 | 0.200 | 26.82 | ---
Case3_1 |  |  | M2 | 102.1 | 102.1 | 0.747 | 1.108 | 0.222 | 22.6 | 22.6
 |  |  | M1 | 34.0 | 136.0 | 0.995 | 1.002 | 0.200 | 27.3 | 4.60
 |  |  | M0 | 0.7 | 136.7 | 1.000 | 1.000 | 0.200 | 27.3 | 
Simulation should be done by using load in Case3_1, but all the simulations in this report were done by using load in Case3. However, it is assumed that the difference is much small.

## Slide 8: Check of brace model

## Slide 9: Soundness of gusset plate
Case5(No reinforcement)
considering self load
case5_1(reinforcement)
considering self load
Result of Self Loading analysis. Contour of equivalent plastic strain
Damage is seen on the gusset plate
Brace has damage for both case if self loading analyses are conducted after installing brace
Damage is seen on the brace

## Slide 10: Soundness of gusset plate
Case5(No reinforcement)
considering self load
case5_1(reinforcement)
considering self load
Result of Self Loading analysis. Contour of equivalent stress
Stress concentration is seen on the gusset plate
Brace has damage for both case if self loading analyses are conducted after installing brace
Stress concentration is seen on the braces and battledores

## Slide 11: Soundness of gusset plate
case5_1 (reinforced)
not considering self load
case5_1(reinforced)
Considering self load
Result of push-over analysis with C0=0.2. Contour of equivalent stress
Braces are not damaged
Braces are damaged

## Slide 12: Progress of damage on brace（case5_1,woSL）
C0=0.4
C0=0.45
C0=0.5
C0=0.6
Braces are not damaged until C0=0.4

## Slide 13: Push-over analysis

## Slide 14: Effect of Self-Weight
For the case applying self load, stiffness is not much increased because damage was seen in the previous self loading analysis.

## Slide 15: Effect of brace
Stiffness of 3F(2nd layer) is 40% larger than the model without brace.

## Slide 16: Effect of reinforcement of gusset plate
Difference is seen in the elastic region. Behavior after damage is almost the same.

## Slide 17: Parameter study for different diameter
Not so big difference is seen between M14 and M16
Simulation for M20 is diverged in an early stage.
I want to decide to use M14 for braces.